m-epics-twincat-ads
TwinCAT 3 integration into EPICS
Anders Sandström, Torsten Bögershausen
www.europeanspallationsource.se
Tuesday, May 22, 2018

---
Overview
HMI (CSS, BOY)
EPCIS CONTROL Network (Channel Access)
Beckhoff controller
 (TwinCAT 3.1)
IOC
 (EPICS, Linux)
ADS
EtherCAT
EtherCAT Coupler
EtherCAT Drive
EtherCAT Coupler
Drive
Analog
Digital
XXXX
Drive
Analog
Digital
XXXX

---
Based on:
  - Beckhoff ADS:	https://github.com/Beckhoff/ADS
  - AsynPortDriver:	https://github.com/epics-modules/asyn/tree/master/asyn/asynPortDriver
- Accessible data:
  - Symbolic access (Main.iTest)
  - Absolute access (adsport, group, offset)
  - Different Ads Ports:
    - PLC1, PLC2, (851,852,..)
    - Other ADS ports NC (500,…)
- Access types:
  - Read:
    - Subscription ”On change” (I/O intr), selectable sample rate and max delay time
    - Sampled
    - Simple datatypes, Arrays
  - Write
    - Simple datatypes, Arrays
- Timestamp:
  - TwinCAT
  - EPICS
- Motor Record Support
- No licenses needed
- No PLC-code needed for communication

---
Record Definition Example:
Record Definition Example:
record(ai,”IOC:GetFTest"){
  field(PINI, "1")
  field(TSE, -2)
  field(DTYP, "asynFloat64")
  field(INP,  "@asyn($(PORT),0,1)TIMEBASE=PLC/T_DLY_MS=500/TS_MS=10/ADSPORT=851/Main.fTest?")
  field(PREC, "3")
  field(SCAN, “I/O Intr”)
}
- Variable name “Main.fTest”
- Subscribe:	(SCAN=”I/O Intr”)
- Adsport 851:	(ADSPORT=851)
- Read access:	(”?” in end of var name)
- Timestamp in TwinCAT:	(TIMESTAMP=PLC, TSE=-2)
- Check if changed each 10ms:	(TS_MS=10)
- Maximum send buffer delay 500ms:	(T_DLY_MS=500)